{"text_format":"3","workbook":"xlsx","n_sheets":6,"sheets":["总表","电气（站内）","电气（站外）","PLC控制柜","中控","监控"],"read":"whole","date_system":"1900"}

{"sheet":"总表","index":0,"n_rows":27,"n_cols":10,"rows_kept":27,"merged":[[0,0,0,9],[2,2,23,2],[2,9,23,9]]}
["电气、自控、监控系统一览表"]
["序号","名称","规格型号","材质","单位","数量","单价","金额","产地/品牌","备注"]
[1,"1#配电柜（一级配电柜）","（具体规格由厂家根据工艺要求配置确定，户外控制箱加装304不锈钢支架）","碳钢喷塑","台",1,{"$nulls":3},"变频器选用ABB，其余电器元件选用正泰或施耐德。"]
[2,"2#配电柜（一级配电柜）",null,"碳钢喷塑","台",1]
[3,"进水泵控制柜",null,"304户外","台",1]
[4,"污泥循环泵控制柜",null,"304户外","台",1]
[5,"压滤机供料泵控制箱",null,"304户外","台",1]
[6,"污水提升泵控制箱",null,"304户外","台",1]
[7,"回用水泵控制箱",null,"304户外","台",1]
[8,"照明控制箱",null,"碳钢喷塑","台",1]
[9,"PLC控制柜",null,"碳钢喷塑","台",1]
[10,"CT01控制箱",null,"304户外","台",1]
[11,"CT02控制箱",null,"304户外","台",1]
[12,"CT03控制箱",null,"304户外","台",1]
[13,"CT04控制箱",null,"304户外","台",1]
[14,"CT05控制箱",null,"304户外","台",1]
[15,"CT06控制箱",null,"304户外","台",1]
[16,"CT07控制箱",null,"304户外","台",1]
[17,"CT08控制箱",null,"304户外","台",1]
[18,"CT09控制箱",null,"304户外","台",1]
[19,"CT10控制箱",null,"304户外","台",1]
[20,"CT11控制箱",null,"304户外","台",1]
[21,"CT12控制箱",null,"304户外","台",1]
[22,"CT13控制箱",null,"304户外","台",1]
[23,"中控系统","（详见清单）",null,"套",1,{"$nulls":3},"西门子"]
[24,"监控系统","（详见清单）",null,"套",1]
[25,"合  计"]

{"sheet":"电气（站内）","index":1,"n_rows":35,"n_cols":9,"rows_kept":35,"merged":[[0,0,0,8],[2,0,34,0],[2,1,3,1],[4,1,6,1],[7,1,9,1],[8,2,9,2],[8,8,9,8],[10,1,11,1],[10,5,11,5],[10,8,11,8],[12,1,14,1],[12,2,14,2],[12,8,14,8],[15,1,17,1],[15,2,17,2],[15,8,17,8],[18,1,20,1],[18,2,20,2],[18,8,20,8],[21,1,22,1],[21,2,22,2],[21,8,22,8],[23,1,24,1],[23,2,24,2],[23,5,24,5],[23,8,24,8],[29,1,34,1]]}
["内部电气仪控制条件一览表"]
["一级控制柜","二级控制柜","三级控制柜","设备名称","规格型号","电气条件","单位","数量","备注"]
["一级配电柜（暂定两台可按实际需求合理配置设计，置于配电房内，碳钢喷塑）","进水泵控制柜","/","进水泵","N=2.2kw，AC380V","变频控制，就地，远程","台",4]
[null,null,"潜水搅拌机控制箱","潜水搅拌机","N=1.5kw，AC380V","就地，远程","台",1,"304户外"]
[null,"污泥循环泵控制柜","/","污泥循环泵","N=1.1kw，AC380V","变频控制，就地，远程","台",4,"304户外"]
[null,null,"刮泥机控制箱（4套）","刮泥机","N=4kw，AC380V","仅供电","台",4,"（设备厂家配套）"]
[null,null,"污泥提升泵控制箱","污泥提升泵","N=2.2kw,AC380V","就地，远程（浮球液位控制）","台",1,"304户外"]
[null,"压滤机供料泵控制箱","/","压滤机供料泵","N=4kw，AC380V","变频控制（一控二），就地，远程","台",2,"304户外"]
[null,null,"污泥搅拌控制箱","潜水搅拌机","N=0.85kw，AC380V","就地","台",1,"304户外"]
[{"$nulls":3},"桨叶式搅拌机","N=4kw，AC380V","就地","台",1]
[null,"板框压滤机控制箱","/","板框压滤机","N=7.5kW，AC380V","仅供电","台",1,"（设备厂家配套）"]
[null,null,"/","压榨水泵","N=1.5kW，AC380V",null,"台",2]
[null,"PAC装置控制箱","/","电磁隔膜计量泵","N=60W，AC220V","远程、就地控制","台",4,"（设备厂家配套）"]
[{"$nulls":3},"PAC罐液位计","DC24V，4-20mA输出","远程、指示与报警","台",1]
[{"$nulls":3},"搅拌器","N=0.55kW,AC380V","远程、就地控制","台",1]
[null,"氧化剂装置控制箱","/","电磁隔膜计量泵","N=30W，AC220V","远程、就地控制","台",4,"（设备厂家配套）"]
[{"$nulls":3},"氧化剂罐液位计","DC24V，4-20mA输出","远程、指示与报警","台",1]
[{"$nulls":3},"搅拌器","N=0.55kW,AC380V","远程、就地控制","台",1]
[null,"重捕剂装置控制箱","/","电磁隔膜计量泵","N=30W，AC220V","远程、就地控制","台",4,"（设备厂家配套）"]
[{"$nulls":3},"重捕剂罐液位计","DC24V，4-20mA输出","远程、指示与报警","台",1]
[{"$nulls":3},"搅拌器","N=0.55kW,AC380V","远程、就地控制","台",1]
[null,"PAM-装置控制箱","/","三箱一体投加装置","N=3kW，AC380V","仅供电","套",1,"（设备厂家配套）"]
[{"$nulls":3},"PAM-投加泵","N=1.1kw，AC380V","远程、就地控制","台",4]
[null,"PAM+装置控制箱","/","电磁隔膜计量泵","N=60W，AC220V","仅供电","台",1,"（设备厂家配套）"]
[{"$nulls":3},"PAM+装置液位开关","连杆球阀液位开关，DC24V，低位、低低位开关量输出",null,"套",1]
[null,"污水提升泵控制箱","/","污水提升泵","N=1.1kw,AC380V","就地（浮球液位控制）","台",1]
[null,"回用水泵控制箱","/","回用水泵","N=3kW，AC380V","就地（压力控制）","台",1]
[null,"树脂吸附系统控制柜","/","/","N=30kW，AC380V","/","套",1,"（设备厂家配套）"]
[null,"CT13控制箱","/","/","N=5.5kW，AC380V","变频控制，就地，远程。流量、液位远程指示，配置转换器采用光纤链接于处理站PLC控制系统）","套",1,"不锈钢户外"]
[null,"照明控制箱（置于配电房内，碳钢喷塑）","办公区照明控制箱（成品）","/","N=5kW，AC220V","/","套",1]
[null,null,"设备区照明控制箱（成品）","/","N=10kW，AC220V","/","套",1]
[null,null,"生活区照明控制箱（成品）","/","N=10kW，AC220V","/","套",1]
[null,null,"路灯照明控制箱（成品）","/","N=5kW，AC220V","/","套",1]
[null,null,"生活区空调","/","N=5kW，AC220V","/","套",1]
[null,null,"办公区空调","/","N=10kW，AC220V","/","套",1]

{"sheet":"电气（站外）","index":2,"n_rows":14,"n_cols":14,"rows_kept":14,"merged":[[0,0,0,13],[2,0,13,0],[2,1,8,1],[2,10,13,10],[3,2,8,2],[4,3,8,3],[5,4,8,4],[6,5,8,5],[7,6,8,6],[9,1,10,1],[12,1,13,1],[12,2,13,2]]}
["外部部电仪控制条件一览表"]
["一级控制柜","二级控制柜","三级控制柜",{"$nulls":5},"设备名称","规格型号","电气条件","单位","数量","备注"]
["成套变压装置（厂家配套）","CT03控制箱","/","/","/","/","/","/","提升泵","N=4kw，AC380V","变频控制，就地，远程。流量、液位远程指示，配置转换器采用光纤链接于处理站PLC控制系统。视频监控系统一并接入。）","台",1]
[null,null,"CT04控制箱","/","/","/","/","/","提升泵","N=4kw，AC380V",null,"台",1]
[{"$nulls":3},"CT05控制箱","/","/","/","/","提升泵","N=7.5kw，AC380V",null,"台",1]
[{"$nulls":4},"CT06控制箱","/","/","/","提升泵","N=7.5kw，AC380V",null,"台",1]
[{"$nulls":5},"CT07控制箱","/","/","提升泵","N=7.5kw，AC380V",null,"台",1]
[{"$nulls":6},"CT08控制箱","/","提升泵","N=7.5kw，AC380V",null,"台",1]
[{"$nulls":7},"CT09控制箱","提升泵","N=7.5kw，AC380V",null,"台",1]
[null,"CT01控制箱","/","/","/","/","/","/","提升泵","N=5.5kw，AC380V",null,"台",1]
[null,null,"CT02控制箱","/","/","/","/","/","提升泵","N=5.5kw，AC380V",null,"台",1]
[null,"CT10控制箱","/","/","/","/","/","/","提升泵","N=5.5kw，AC380V",null,"台",1]
[null,null,"CT11控制箱","/","/","/","/","/","提升泵","N=5.5kw，AC380V",null,"台",1]
[{"$nulls":3},"CT12控制箱","/","/","/","/","提升泵","N=5.5kw，AC380V",null,"台",1]

{"sheet":"PLC控制柜","index":3,"n_rows":16,"n_cols":7,"rows_kept":16,"merged":[[0,0,0,6],[1,1,1,2],[2,1,14,1],[15,0,15,6],[26,0,26,6]]}
["电仪条件表"]
["序号","主要设备",null,"电气条件","单位","数量","备注"]
[1,"PLC控制柜，置于配电房内，碳钢喷塑，链接中控。","排泥阀","DC24V","套",4,"远程控制（配就地控制箱，就地远程）"]
[2,null,"沉淀池进水流量计","DC24V，4-20mA输出","套",4,"供电，远程指示"]
[3,null,"出水流量计","巴歇尔槽，流量范围0-250m³/h；包含液位计等成套设备；","套",1,"供电，远程指示"]
[4,null,"调节水箱液位计","24V,4-20mA输出","台",1,"供电，远程指示"]
[5,null,"储泥水箱液位计","DC24V,4-20mA输出","台",2,"供电，远程指示"]
[6,null,"污水坑液位开关","DC24V","台",2,"供电，远程指示"]
[7,null,"污泥池液位开关","DC24V","台",1,"供电，远程指示"]
[8,null,"混凝沉淀出水箱液位计","DC24V,4-20mA输出","台",1,"供电，远程指示"]
[9,null,"原水浊度计","DC24V，4-20mA输出","套",1,"供电，远程指示"]
[10,null,"沉淀池出水浊度计","DC24V，4-20mA输出","套",4,"供电，远程指示"]
[11,null,"原水pH计","DC24V，4-20mA输出","套",1,"供电，远程指示"]
[12,null,"进水在线检测装置","砷，镉，锰，总磷，总氮，COD，总氮，氨氮","套",7,"远程指示"]
[13,null,"出水在线检测装置","砷，镉，锰，总磷，总氮，COD，总氮，氨氮","套",7,"远程指示"]
["备注：站内、站外电气控制“远程”单元均接入PLC系统。"]

{"sheet":"中控","index":4,"n_rows":14,"n_cols":8,"rows_kept":14,"merged":[[0,0,0,7],[13,0,13,7]]}
["中控设备明细表"]
["序号","产品名称","规格型号","单位","数量","单价","金额","备注"]
[1,"数据服务器","Xeon E5405 2.8Hz双核服务器","台",1,null,{"$f":"F3*E3","v":{"v":0,"d":"0.00"}}]
[2,"监控操作计算机/工程师站","i5,3.2G LED 24''","台",2,null,{"v":0,"d":"0.00"}]
[3,"PLC编程软件包","与PLC配套","套",1,null,{"v":0,"d":"0.00"}]
[4,"组态软件运行版","1024点","套",2,null,{"v":0,"d":"0.00"}]
[5,"组态软件开发版","1024点","套",1,null,{"v":0,"d":"0.00"}]
[6,"打印机（报价、报表）","彩色激打，A3,网络打印机","台",1,null,{"v":0,"d":"0.00"},"惠普"]
[7,"中心千兆工业以太网交换机","模块式，1000M 一光三电/100M二光十电","台",1,null,{"v":0,"d":"0.00"}]
[8,"工业网络交换机","多模 二光六电","套",1,null,{"v":0,"d":"0.00"}]
[9,"中央控制台","3000宽×1200高×800深，钢制","面",1,null,{"v":0,"d":"0.00"},"含座椅"]
[10,"便携式编程终端","含接口适配器","台",1,null,{"v":0,"d":"0.00"}]
[11,"硬件防火墙","支持VPN,入侵检测：DOS,DDOS","套",1,null,{"v":0,"d":"0.00"}]
["注：上述附属配置均供参考，具体可由厂家二次深化。（含安装调试）"]

{"sheet":"监控","index":5,"n_rows":20,"n_cols":9,"rows_kept":20,"merged":[[0,0,0,8],[19,0,19,7]]}
["监控系统一览表"]
["序号","名称","型号及规格","单位","数量","品牌","单价","金额","备注"]
[1,"录像机32路","海康威视32路8盘位网络硬盘录像机","套",1,"海康威视",null,{"$f":"G3*E3","v":0}]
[2,"硬盘","3TB","个",2,"西部",null,{"$f":"G4*E4","v":0}]
[3,"监控电脑","戴尔(DELL)灵越3670 高性能 台式电脑主机(九代i7-9700 8G+16G","台",2,"DELL",null,{"$f":"G5*E5","v":0}]
[4,"海康球机控制键盘三维操作",null,"套",1,"海康威视",null,0]
[5,"数字低照度快球摄像机","最低照度：彩色0.3Lux,黑白0.08Lux（红外LED打开）；焦距/变焦P倍数4.45mm-89mm/20X；分辨率：1280*720P(HD)","套",3,"海康威视",null,0,"站内户外。"]
[6,"数字枪式摄像机","室内,彩色一体化定位系统,3.8~91.2mm,0.05Lux","套",14,"海康威视",null,0,"13套站外，一套室内。"]
[7,"防雷","百兆  二合一","台",17,"国产",null,0]
[8,"光纤收发器","TL-FC111A","对",17,"TP-LINK",null,0]
[9,"千兆以太网交换机","48电4光","台",1,"TP-LINK",null,0]
[10,"安防电源","DC24V电源","只",17,"国产",null,0]
[11,"光纤跳线","SC接口","根",34,"国产",null,0]
[12,"就地保护箱","200*150*100","台",17,"定制",null,0]
[13,"室外安装支架","含立杆","个",16,"国产",null,0]
[14,"室内安装支架",null,"个",1,"国产",null,0]
[15,"交换机","8口千兆交换机","台",3,"TP-LINK",null,0]
[16,"UPS","10KVA，60min","台",1,"山特",null,0]
[17,"合  计"]
["注：上述附属配置均供参考，在保证摄像机数量及监控需求的基础上，具体由厂家二次深化。（含安装调试）"]